5. PROJECT NUMBER (if applicable)

CODE

7. ADMINISTERED BY

2. AMENDMENT/MODIFICATION NUMBER

CODE

6. ISSUED BY

8. NAME AND ADDRESS OF CONTRACTOR

4. REQUISITION/PURCHASE REQ. NUMBER

3. EFFECTIVE DATE

9A. AMENDMENT OF SOLICITATION NUMBER

9B. DATED

PAGE        OF     PAGES

10A. MODIFICATION OF CONTRACT/ORDER NUMBER

10B. DATED

BPA NO.

1. CONTRACT ID CODE

FACILITY CODE

CODE

Offers must acknowledge receipt of this amendment prior to the hour and date specified in the solicitation or as amended, by one of the following methods:

The above numbered solicitation is amended as set forth in Item 14.  The hour and date specified for receipt of Offers

E. IMPORTANT:

is extended,

(a) By completing Items 8 and 15, and returning __________ copies of the amendment; (b) By acknowledging receipt of this amendment on each copy of the

offer submitted; or (c) By separate letter or electronic communication which includes a reference to the solicitation and amendment numbers.  FAILURE OF YOUR

ACKNOWLEDGMENT TO BE RECEIVED AT THE PLACE DESIGNATED FOR THE RECEIPT OF OFFERS PRIOR TO THE HOUR AND DATE SPECIFIED MAY

is not extended.

12. ACCOUNTING AND APPROPRIATION DATA

(REV. 11/2016)

is required to sign this document and return ___________ copies to the issuing office.

is not,

A. THIS CHANGE ORDER IS ISSUED PURSUANT TO:    (Specify authority)   THE CHANGES SET FORTH IN ITEM 14 ARE MADE IN THE CONTRACT ORDER NO. IN ITEM 10A.

15C. DATE SIGNED

B. THE ABOVE NUMBERED CONTRACT/ORDER IS MODIFIED TO REFLECT THE ADMINISTRATIVE CHANGES

SET FORTH IN ITEM 14, PURSUANT TO THE AUTHORITY OF FAR 43.103(b).

RESULT IN REJECTION OF YOUR OFFER.  If by virtue of this amendment you desire to change an offer already submitted, such change may be made by letter

or electronic communication, provided each letter or electronic communication makes reference to the solicitation and this amendment, and is received prior to

the opening hour and date specified.

C. THIS SUPPLEMENTAL AGREEMENT IS ENTERED INTO PURSUANT TO AUTHORITY OF:

D. OTHER

Contractor

16C. DATE SIGNED

14. DESCRIPTION OF AMENDMENT/MODIFICATION

16B. UNITED STATES OF AMERICA

Except as provided herein, all terms and conditions of the document referenced in Item 9A or 10A, as heretofore changed, remains unchanged and in full force and effect.

15A. NAME AND TITLE OF SIGNER

16A. NAME AND TITLE OF CONTRACTING OFFICER

15B. CONTRACTOR/OFFEROR

STANDARD FORM 30

PREVIOUS EDITION NOT USABLE

Prescribed by GSA - FAR (48 CFR) 53.243

(Type or print)

(Type or print)

(Organized by UCF section headings, including solicitation/contract subject matter where feasible.)

(Number, street, county, State and ZIP Code)

(If other than Item 6)

(Specify type of modification and authority)

(such as changes in paying office, appropriation date, etc.)

(If required)

(SEE ITEM 11)

(SEE ITEM 13)

(X)

CHECK

ONE

13. THIS ITEM APPLIES ONLY TO MODIFICATIONS OF CONTRACTS/ORDERS,

IT MODIFIES THE CONTRACT/ORDER NO. AS DESCRIBED IN ITEM 14.

11. THIS ITEM ONLY APPLIES TO AMENDMENTS OF SOLICITATIONS

AMENDMENT OF SOLICITATION/MODIFICATION OF CONTRACT

(Signature of person authorized to sign)

(Signature of Contracting Officer)

1

5

0002

11-07-2025

none

36C260

Network Contracting Office 20

ATTN: V4CONT

1601 E. Fourth Plain Blvd

Bldg.17, Suite B428

Vancouver WA 98661

To all Offerors/Bidders

36C26026Q0034

10-27-2025

X

X

X

1

X

The purpose of this amendment is to answer industry questions.

See continuation pages for industry questions and governement responses.

All other terms and conditions remain the same.

Derek Crockett

1.) May I formally request the following information

incumbent contract #

Site Visit sign in sheet

Answer: There is no incumbent contract for this requirement. The government will not be disclosing which firms attended the site visit for this solicitation.

2.) Is the awarded contractor responsible “cleaning and punching tubes” of only the condenser?

Answer: The condenser tubes need to punched annually.

- Is the award contractor expected to ” cleaning and punching tubes” of the evaporator?

  - If yes, Please provide frequency

Answer: The evaporator tubes need to be punched every two years in accordance with manufacturer and agency regulations and guidelines. The contractor will be required to punch the evaporator tubes once in 2026 and once in 2028.

3.) Is he awarded contractor expected to provide and coordinate Eddy Current on both the condenser and evaporator?

  - If yes, Please provide frequency along with a schedule.

Answer: The contractor shall ensure all work adhere to Eddy Current’s manufacturer recommendations and guidelines for maintenance of Chiller performance. Therefore, coordination with Eddy Current may be required by the contractor.

4.) Is the awarded contractor responsible for vibration analysis of the chillers, pumps and cooling towers? If yes, please provide frequency along with a schedule.

Answer: Vibration analysis may be required for certain chillers and pumps based on manufacturer guidelines and recommendations.

5.) Pumps: Is the government requesting vibration analysis twice per year?

Answer: Frequency will be based on manufacturer recommendations and guidelines of the equipment and industry standards. The contractor’s vibration analysis and work performed will be subject to COR review and approval to determine if compliance and adherence have been met.

Are the pumps being controlled by VFD’s?

    - If yes are the associated VFD’s included in the preventive maintenance contract?

Answer: Yes, the pumps are controlled by VFDs. VFDs will need to be tested and inspected semiannually.

  - The last line of Section 3 states "Inspect pump seals and replace/repair where needed. Can the government please confirm any and all repairs will require a proposal and the awarded contractor will receive a contract modification or a separate PO to proceed?

Answer: The contractor is responsible for inspecting pumps and seals and providing routine preventative maintenance semiannually or twice a year. Any repairs or replacements that are outside of the scope of routine maintenance (lubricating the pumps, checking seals, coupling alignment, and other preventative maintenance tasks) require the contractor to provide a quote for repairs in the reporting deliverables and as outlined in the statement of work.

6.) Cooling tower: Are the cooling towers controlled by VFD? If yes are the associated VFD’s included in the preventive maintenance contract?

Answer: Yes, the cooling towers are controlled by VFD. VFDs will need to be tested and inspected semiannually.

During the cleaning process does the government require a pre and post disinfection?

Answer: Pre or Post disinfection will only be required if outlined in the equipment manufacturer specifications and guidelines.

7.) Is the awarded contractor responsible for any water treatment associated with the chillers cooling towers or pumps?  If yes, Please provide equipment information and scope of work.

Answer: No, water treatment is not required.

- Is the awarded contractor responsible for any refrigerant monitors located within the energy center?

Answer: No, the contractor is not required to work or provide maintenance services on the refrigerant monitors.

If yes, Please provide equipment information and scope of work.

Answer: see above.

8.) Is the awarded contractor responsible for any BMS maintenance associated with the chilled water plant?

Answer: Yes, BMS maintenance is required.

  - Calibration of flow meters?

Answer: Yes, that is required by the contractor annually.

  - Calibration of DP’s?

Answer: Yes, that is required by the contractor annually.

  - Calibration of temperature and or pressure transducers created within the chilled water loop of the building?

Answer: Yes, that is required by the contractor annually.

  - BMS system updates or backups?

Answer: BMS system updates and backups are not required by the contractor. In the event, a BMS system update is needed for the contractor to accomplish the inspection, testing, preventative maintenance, and scope of services outlined in the statement of work, then coordination will occur with the VA COR, BMS provider, and the contractor.

  - Will be awarded contractor be given access to the BMS system upon request?

Answer: No, the contractor will not have access to the BMS system

Calibration or tuning of actuated valves?

Answer: Yes, the contractor is required to perform these tasks annually.

9.) Will the government allow the awarded contractor to ship materials and tools to the VA Energy center or shipping and receiving department?

Answer: Yes, a lay down area and storage area for contractor materials may be allowable and is subject to prior COR review and approval. However, the contractor shall be responsible for all its equipment and supplies. And the contractor shall be responsible for all removal and movement of supplies required to complete the work.

- What government Provide space for the awarded contractor to store equipment? Example 60” x 30” gang box.

Answer: Yes, a gang box is available but is subject to prior COR approval.

- Will the government provide lockout tag out in accordance with NFPA 70E

Answer: The contractor shall provide all lockout tags when required.

- Can the government please provide a clear expectation for the annual task of “Refrigerant level”?

Answer: The contractor shall inspect the refrigerant for leak checks semiannually.

10.) Is the awarding contractor expected to recover and weigh the refrigerant annually?

Answer: No, the contractor is not required to recover and weigh the refrigerant. If there is deficiencies such as leaks and other deficiencies identified during the semiannual inspection, the contractor shall submit the findings on the semi-annual reports and provide a quote that includes recommended maintenance and repairs and costs.

11.) Section 6 contractor schedule:

  - Can the government please confirm that all isolation valves are in good operating condition And will allow for isolation?

Answer: The isolation valves are currently operational. However, the contractor is responsible for providing semiannual inspection, testing, and preventative maintenance on the isolation values and reporting any deficiencies in submission of the semi-annual reports.

    - If the valves do not provide proper isolation how will the government proceed?

Answer: The contractor shall provide a quote after the semiannual inspecting, testing, and preventative maintenance and that outlined and documents all deficiencies on the semiannual report.

12. Are there any items on the semi-annual tasking list that could be done annually instead? Some of the items are typically done once a year on a chiller maintenance. Could the following items be completed annually instead of semi-annually?

- Inspect and record compressor-motor assembly voltage and resistance.

- Lubricate open motors and align open drive units.

- Replace oil filter/dryer; perform oil analysis.

- VSD inspection, recalibration, and coolant fluid replacement.

Answer: The contractor must perform the tasks listed in questions 12. semiannually.

13.)  Can the offeror rely on subcontractor certifications to satisfy the requirements stated in the solicitation?

Answer: The government cannot advise interested parties or offerors on subcontractor personnel relationships or structures; offerors will be evaluated in accordance with the solicitation terms and conditions.

14.)  Please confirm the submission inbox/portal (and any size/format limits).

Answer: Please limit offeror emailed submissions to 40MB. Interested parties may submit offeror submission requirements on or before the close date of 11/14/2025 at 14:00 PST directly to derek.crockett@va.gov. Offers will be accepted by email only.

15.) The RFQ/SOW lists the Place of Performance as Seattle 98108; the cover page also references 98018. Please confirm the correct ZIP (we will use 98108 absent further direction).

Answer: The zip code is 98108 for the Puget Sound VA Medical Center – Seattle Campus.

15. Wage Determinations: RFQ notes SCA/SCLS Wage Determinations (King County, WA); please confirm the current WD number and revision to apply at award.

Answer: The most recent Department of Labor (DOL) Wage Determination for King, County Washington at time of award will be listed in the award document. Attachment SCA WAGE DETERMINATIONS KING COUNTY WA.docx on www.sam.gov, under notice ID: 36C26026Q0034, displays the current wage determinations “Service Contract Act WD # 2015-5535” for King County Washington or the place of performance.