## DIRECTIONS
TAILORED COMMENT MATRIX
THIS DOCUMENT MUST BE RETURNED IN A MICROSOFT EXCEL FILE FORMAT. DO NOT RETURN YOUR RESPONSES IN ANY DIFFERENT FILE FORMAT.
Directions & Explanation of TAILORED COMMENT MATRIX
This Tailored Comment Matrix is provided in order for potential offerors to provide feedback, comments, and ask questions with regard to the released RFP. The sheet labeled "DIRECTIONS" explains this document, and provides directions for its use. The sheet labeled "MATRIX" contains a table with all labeled and numbered elements from the RFP. This table is where potential offerors may respond to the Government with feedback, comments, or ask questions.
Directions and explanation of sheet labeled "MATRIX"
The MATRIX sheet can be reached by clicking the "MATRIX" Tab at the bottom of this spreadsheet. Add rows as necessary under the applicable item.
MATRIX COLUMN DESCRIPTIONS:
Column A: | Contains the Item reference number for this item. This number is used for organizational purposes, when referring to this document only.
Column B: | Contains the section number that each element is labeled, within their respective documents. The section number relates directly to the item's location in the RFP.
Column C: | Contains the written title for the corresponding item/section number.
Column D: | Contains a drop down box for selecting the type of comment. Available options are "Critical" "Substantive" or "Administrative".
Critical: Violations of law -or- Unnecessary risks to safety, life & limb, or VA Material; waste or abuse of VHA appropriations; unreasonable burden on resources.
Substantive: Appears or is potentially unnecessary, incorrect, misleading, confusing, or inconsistent with other sections; disagree with proposed responsibilities, requirements, and/or procedures.
Administrative: Address typographical, grammatical, and formatting errors (grammar, punctuation, style, etc.)
Column E: | Contains recieved date of offerors' comments/questions/responses.
Column F: | Contains space for potential offerors' comments/questions/responses.
Column G: | Contains space for VHA comments/questions/responses.
Column H: | Contains response date for VHA comments/questions/responses.
Column I: | Contains VHA Section/ POC shop comments/questions/response
Column J: | Contains Contractor Name requesting /questions/responses.
THIS DOCUMENT MUST BE RETURNED IN A MICROSOFT EXCEL FILE FORMAT. DO NOT RETURN YOUR RESPONSES IN ANY DIFFERENT FILE FORMAT.

## MATRIX
ITEM # | SECTION or ATTACHMENT # | DOCUMENT NAME | COMMENT TYPE (Select from drop down) | Received Date | QUESTIONS / COMMENTS (With justification of why considered source selection sensitive if applicable) | VA Response | Response Date | VA Response From
1 |  |  |  | 2025-09-22 | Please confirm that specification section 030130.2.1.C.1 & 3 stated minimum FRP properties are the "Dry Properties" and not the "Laminate Properties". The listed manufactures do not have a product meeting these laminate properties. | Correct. 18oz/sqyd is acceptable. Products such as Sika HEX-103 C, Mapei MapeWrap C Uni-Ax 600, or similar are acceptable. |  | A/E
2 |  |  |  | 2025-09-22 | The specification section 030130.2.1.C.2 & 4 stated minimum FRP properties for Tensile Modulus and Dry fabric Weight corresponds to a Unidirectional Glass fabric, Please confirm it is acceptable to use the V-wrap EG50 Unidirectional glass fabric by Structural Technologies. This product exceeds the minimum Tensile Modulus listed and this product line carries an ICC approval. | 18oz/sqyd is acceptable. Products such as Sika HEX-103 C, Mapei MapeWrap C Uni-Ax 600, or similar are acceptable. |  | A/E
3 |  |  |  | 2025-09-22 | At the site visit, it was discussed that for this project, the air exchange currently in place from the mechanical contractor, Robbins and Morton, working in the same area will be utilized for that area for the awarded contractor to utilize for this project. Will we have access to air exchange for the full duration of this project, and if not, how long will the mechanical contractor keep their air exchange on site? | The contractor should plan to provide the equipment for the air exchange requirements for the duration of the period of performance, as required. |  | VA
4 |  |  |  | 2025-09-22 | If the means and methods provided to us in details on drawings disrupt the canteen/kitchen overhead, will we be provided additional means and methods to complete the work, or will the kitchen/canteen be moved to a temporary location? | The contractor will be required to adjust their schedule to off-hours work for actions that will be too disruptive and interfere with operations. Expect up to 25% of the work to occur after hours or weekends. The contractor shall provide a daily cost for 25% after hours/weekend work as a line item in the proposal. |  | VA
5 |  |  |  | 2025-09-22 | In the event shoring is brought in to the below grade areas, are we allowed to modify the opening around the existing air exchange on the East Side of the building to bring shoring in and return the area to the existing finish once completed? | More detail on the proposed modifications is required for approval. The contractor shall submit detailed information on proposed work post-bid. Any modifications to openings shall be designed by the contractor's engineer of record. |  | A/E
6 |  |  |  | 2025-09-22 | Is there any coordination that will be required that we need to be aware of to accommodate the mechanical contractor or will we have full access as needed for this project throughout the area? | The contractor will have full access to the space to complete the work. |  | VA
7 |  |  |  | 2025-09-22 | If Robbins and Morton is in the same working space that we are, will dance floors (platforms) set up over the ground level MEP to facilitate access for overhead repairs prohibit their work from being completed? | The structural repair contractor will have full access to the space during concrete repair activities. Structural repair work will have priority. Well-defined work plans, 3-week lookahead schedules, and work execution plans will be required and shall be shared to coordinate activities. |  | VA
8 |  |  |  | 2025-09-22 | During the site visit, there were areas that were pointed out of which asbestos insulation has been encapsulated. For the encapsulated asbestos areas, there are multiple locations where the encapsulation has already failed. To avoid further risk of exposure, will the areas where work is to be completed by this project be abated prior to mobilization for this project by the VAMC (or others) under a separate contract, or will it be contractor responsibility to include this abatement in our proposal? | The successful bidder shall be responsible for installing containment they feel is necessary for the safe execution of this project. |  | VA
9 |  |  |  | 2025-09-22 | Are there additional documents available for this project? On the site visit on 9/18/2025 there were drawings outlining column locations that have not been provided on sam.gov. | See S104 of Bid Documents. This sheet is provided to aid in wayfinding in the crawlspace. Note that the majority of the columns in the space have markings of either grid coordinates or column numbers corresponding to the information on S104 on them. |  | A/E & VA
10 |  |  |  | 2025-09-22 | Will we have access to all current structural/consultant reports on the location of repairs? | The contract documents are sufficient for the implementation of the work under this project. The JS Held report information is provided as an adjunct to the repair drawings and not all of the deficiencies identified by the previous assessment are being repaired. |  | VA
11 |  |  |  | 2025-09-22 | Will the current lighting plan in the basement remain during construction or are we responsible for providing our own lighting? | The Contractor must determine if the available lighting is sufficient to complete the work. If additional lighting is required, the Contractor must provide it. |  | VA
12 |  |  |  | 2025-09-22 | There are conflicting concrete coverage acceptance rates. What is the true column and joist concrete coverage? | 3/4" Minimum. See updated S105. |  | A/E
13 |  |  |  | 2025-09-22 | When it comes to conflicts between the JS Held Report and some of the drawings seen during the site visit on 9/18/2025, which are we to defer to when building our proposal? | The Bid Documents take precedence over the JS Held Information. The JS Held report information is provided for reference only and as an adjunct to the repair drawings and not all of the deficiencies identified by the previous assessment are being repaired. |  | A/E
14 |  |  |  | 2025-09-22 | On the documents provided to us in the Enlarged Repair Notes, 4 states that the quantities are to be verified and determined by the contractor (see photo below). Will there be base quantities provided for the initial bid and all the work discovered will be qualified as change orders during the work? | Base quantities are indicated on the tags. See the Deficiency Legend for the location of the quantities on the tag. |  | A/E
15 |  |  |  | 2025-09-22 | Is this work area considered confined space? | Yes. A daily permit will be required. Safety will provide this permit. They are located in Building 24, 2nd floor. The instructions and forms are located in the Attachment 10 of the solicitation SOP 516-138S-010 - Confined Space Program. |  | VA
16 |  |  |  | 2025-09-22 | What are the SSHO Requirements for this project? Is there certain certifications or experience? Can the SSHO be dual hat of other responsibilities? If not, is it required to be a full-time position? We want to price it to meet the staffing requirements of the VAMC for this project. | Refer to pages 7 and 8 of the RFP of this solicitation and the safety specifications. No, the SSHO cannot dual-hat. This project has a confined space component. |  | A/E & VA
17 |  |  |  | 2025-09-22 | During the site visit on 9/18/2025 it was stated that daily safety permits will be required for this project. What does this process consist of and how many workers does one permit cover? And can the VA provide more clarification on what is involved in the daily safety permits required for work? | Daily confined space permit. See response in item 15. |  | VA
18 |  |  |  | 2025-09-22 | Are there defined work hours for this project? If so, are the hours flexibility to allow for evening and weekend work hours at the discretion of the contractor? | Generally, this project's work hours will be 0700 to 1700 M-F, excluding Federal Holidays. Any work outside these hours shall be coordinated with the COR 14 calendar days in advance. |  | VA
19 |  |  |  | 2025-09-22 | There are notes outlining potential special inspections for this project. What specific special inspections are required and is there a preferred or required vendor for these 3rd party inspections? | See section L of the "Schedule of Special Inspections" in the specification manual for specific special inspection requirements (section 01 45 35). Note that "concrete" refers to a material with cement-based binders and both large and small aggregates. "Repair Mortar" is a specialized material lacking large aggregate. Requirements for repair mortar quality control can be found in 03 32 00. Refer to page 8 of the RFP of this solicitation for qualifications. |  | A/E & VA
20 |  |  |  | 2025-09-22 | What are the badging requirements at this facility as far as any forms or basic employee info? How far in advance prior to showing up first day is the employee list and information required to be provided to your security/badging office? | The contractor is required to provide a sign-in sheet every day. The information will be shared with CFM's Resident Engineer. |  | VA
21 |  |  |  | 2025-09-22 | Is there a US citizen requirement for all onsite staff of the contractor? | See Clause 52.222-54 in the solicitation.
22 |  |  |  | 2025-09-23 | Could you please provide a copy of the shoring plans detailing the precise locations of the poles? | Shoring during construction is to be performed by contractor. Shoring is required at areas that require an annular space around reinforcement, which may not have been immediately clear during site investigations. The contractor shall provide temporary shoring shop drawings to facilitate the performance of permanent repairs for this project. The project is designed to permanently repair the critical areas in the construction documents. |  | A/E
23 |  |  |  | 2025-09-23 | Could you please provide the critical areas requiring shoring plans for building 1? The plans that the onsite rep had yesterday at the site visit. | We have provided an updated set of drawings as part of these responses that includes the requested information. |  | A/E
24 |  |  |  | 2025-09-23 | Is there a shoring bid sheet available? | No. See response in item 22. |  | A/E & VA
25 |  |  |  | 2025-09-23 | Will all shoring be conducted simultaneously, or will it be performed in sections as work is completed in each area? | The amount of shoring installed at any single point will be determined by the contractor. Because of the congestion, it is anticipated that only the immediate work area will be shored, then those shores relocated after the repairs achieve adequate strength. Repair materials specified have a high early strength to minimize the amount of time any shoring has to remain in place. |  | A/E
26 |  |  |  | 2025-09-23 | While onsite yesterday we noted multiple signs warning of asbestos. Was an asbestos test completed for air quality? | All information regarding hazardous materials has been or will be shared. Ultimately, it is the responsibility of the contractor to provide a safe working environment. Costs associated with environmental conditioning should be noted accordingly in the bidder's proposal. |  | VA
27 |  |  |  | 2025-09-23 | Is there a specific shoring engineer? | No, there is not a specific shoring engineer. See also the response on Item 22. |  | A/E & VA
28 |  |  |  | 2025-09-24 | Will the construction require structural certification after completion? | Yes.The Special Inspector shall certiy all work subject to special inspections. The Special Inspector must be a Registered Professional Engineer in the State of Florida on the state special inspector’s list. Completion of this project is contingent upon results of special inspections, construction materials testing and engineer of record observations.
29 |  |  |  |  | Is there a specific phasing plan? | No, however the contractor shall begin with repair work of column #173A first (see sheets S103, S105, and spec section 01 00 00 paragraph H), and then develop their work plan from there.
30 |  |  |  |  | What documents must be submitted prior to NTP? | Contractor shall submit Accident Prevention Plan, insurance, bond, project cost-loaded schedule, confined space training certificates for all workers who will enter the crawlspace, and quality plan within 10 calendar days. Contractor may also submit material submittals immediately after contract award.
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93

## Sheet1
Solicitation 36C24825R0168
516-23-604, BB - Install Temp Shoring in Crawl Space at Building 1 (Structural Repairs)
Requests for Information
Question 1. | Please confirm that specification section 030130.2.1.C.1 & 3 stated minimum FRP properties are the "Dry Properties" and not the "Laminate Properties". The listed manufactures do not have a product meeting these laminate properties.
Question 2. | The specification section 030130.2.1.C.2 & 4 stated minimum FRP properties for Tensile Modulus and Dry fabric Weight corresponds to a Unidirectional Glass fabric, Please confirm it is acceptable to use the V-wrap EG50 Unidirectional glass fabric by Structural Technologies. This product exceeds the minimum Tensile Modulus listed and this product line carries an ICC approval.
Question 3. | At the site visit, it was discussed that for this project, the air exchange currently in place from the mechanical contractor, Robbins and Morton, working in the same area will be utilized for that area for the awarded contractor to utilize for this project. Will we have access to air exchange for the full duration of this project, and if not, how long will the mechanical contractor keep their air exchange on site?
Question 4. | If the means and methods provided to us in details on drawings disrupt the canteen/kitchen overhead, will we be provided additional means and methods to complete the work, or will the kitchen/canteen be moved to a temporary location?
Question 5. | In the event shoring is brought in to the below grade areas, are we allowed to modify the opening around the existing air exchange on the East Side of the building to bring shoring in and return the area to the existing finish once completed?
Question 6. | Is there any coordination that will be required that we need to be aware of to accommodate the mechanical contractor or will we have full access as needed for this project throughout the area?
Question 7. | If Robbins and Morton is in the same working space that we are, will dance floors (platforms) set up over the ground level MEP to facilitate access for overhead repairs prohibit their work from being completed?
Question 8. | During the site visit, there were areas that were pointed out of which asbestos insulation has been encapsulated. For the encapsulated asbestos areas, there are multiple locations where the encapsulation has already failed. To avoid further risk of exposure, will the areas where work is to be completed by this project be abated prior to mobilization for this project by the VAMC (or others) under a separate contract, or will it be contractor responsibility to include this abatement in our proposal?
Question 9. | Are there additional documents available for this project? On the site visit on 9/18/2025 there were drawings outlining column locations that have not been provided on sam.gov.
Question 10. | Will we have access to all current structural/consultant reports on the location of repairs?
Question 11. | Will the current lighting plan in the basement remain during construction or are we responsible for providing our own lighting?
Question 12. | There are conflicting concrete coverage acceptance rates. What is the true column and joist concrete coverage?
Question 13. | When it comes to conflicts between the JS Held Report and some of the drawings seen during the site visit on 9/18/2025, which are we to defer to when building our proposal?
Question 14. | On the documents provided to us in the Enlarged Repair Notes, 4 states that the quantities are to be verified and determined by the contractor (see photo below). Will there be base quantities provided for the initial bid and all the work discovered will be qualified as change orders during the work?
Question 15. | Is this work area considered confined space?
Question 16. | What are the SSHO Requirements for this project? Is there certain certifications or experience? Can the SSHO be dual hat of other responsibilities? If not, is it required to be a full-time position? We want to price it to meet the staffing requirements of the VAMC for this project.
Question 17. | During the site visit on 9/18/2025 it was stated that daily safety permits will be required for this project. What does this process consist of and how many workers does one permit cover? And can the VA provide more clarification on what is involved in the daily safety permits required for work?
Question 18. | Are there defined work hours for this project? If so, are the hours flexibility to allow for evening and weekend work hours at the discretion of the contractor?
Question 19. | There are notes outlining potential special inspections for this project. What specific special inspections are required and is there a preferred or required vendor for these 3rd party inspections?
Question 20. | What are the badging requirements at this facility as far as any forms or basic employee info? How far in advance prior to showing up first day is the employee list and information required to be provided to your security/badging office?
Question 21. | Is there a US citizen requirement for all onsite staff of the contractor?
Response: See Clause 52.222-54 in the solicitation.
Question 22. | Could you please provide a copy of the shoring plans detailing the precise locations of the poles?
Question 23. | Could you please provide the critical areas requiring shoring plans for building 1? The plans that the onsite rep had yesterday at the site visit.
Question 24. | Is there a shoring bid sheet available?
Question 25. | Will all shoring be conducted simultaneously, or will it be performed in sections as work is completed in each area?
Question 26. | While onsite yesterday we noted multiple signs warning of asbestos. Was an asbestos test completed for air quality?
Question 27. | Is there a specific shoring engineer?