## Routine Elevator Service calls
Approved Date | Work Type | Description | Location
Jun 6, 2023, 10:43 AM | ROUTINE | ELEVATOR INSPECTION: ELEVATOR UNIT 5, MIDDLE OF BUILDING - TOP OF ELEVATOR - ADJUST DEAD END CLAMPS TO A MAXIMUM HEIGHT OF 4X AND 8X THE DIAMETER OF | NEWLON-86
Jun 6, 2023, 1:39 PM | ROUTINE | ELEVATOR INSPECTION: ELEVATOR UNIT 5, MIDDLE OF BLDG - TOP OF ELEVATOR - CAR-TOP STOP SWITCH SHALL BE ACCESSIBLE FROM LANDING AS PER A17.1 2.26.1.4.2 | NEWLON-86
Jun 6, 2023, 10:23 AM | ROUTINE | ELEVATOR INSPECTION: ELEVATOR UNIT 7, SOUTH OF BLDG - ELEVATOR PIT - ADJUST SWITCH OPERATION SO THE NORMAL LIMIT ACTIVATES PRIOR TO THE FINAL LIMIT | NEWLON-87
Jun 6, 2023, 10:14 AM | ROUTINE | ELEVATOR INSPECTION: ELEVATOR UNIT 5, MIDDLE OF BLDG - TOP OF ELEVATOR - TWO SPEED DOOR CLIPS ARE MISSING ON HOISTWAY DOORS. MULTI PANEL DOORS SHALL | NEWLON-86
Jun 6, 2023, 2:26 PM | ROUTINE | ELEVATOR INSPECT: UNIT 36 , WEST SIDE - INSIDE OF ELEVATOR - IN CAR STOP SWITCH ON ALL FREIGHT ELEVATORS WHILE OPENED, SHALL CAUSE THE AUDIBLE DEVICE | NEWLON-456
Jun 6, 2023, 2:10 PM | ROUTINE | ELEVATOR INSPECTION: ELEVATOR UNIT 28, TO THE LEFT OF ENTRANCE - INSIDE OF ELEVATOR - REPAIR INOPERATIVE DOOR CLOSE BUTTON | NEWLON-448
Jun 6, 2023, 10:29 AM | ROUTINE | ELEVATOR INSPECTION: ELEVATOR UNIT 5, MIDDLE OF BUILDING - INSIDE OF ELEVATOR - REPAIR INORPERATIVE EMERGENCY LIGHT/BELL AS PER ASME A17.1 RULE 204.7A | NEWLON-86
Jun 6, 2023, 1:43 PM | ROUTINE | ELEVATOR INSPECTION: ELEVATOR UNIT 7, SOUTH OF BLDG - MACHINE ROOM - MACHINE ROOM PHONE TO CAR IS INOPERATIVE | NEWLON-87
Jun 6, 2023, 11:29 AM | ROUTINE | ELEVATOR INSPECTION: ELEVATOR UNIT 7, SOUTH OF BLDG - TOP OF ELEVATOR - ADJUST DEAD END CLAMPS TO A MAXIMUM HEIGHT OF 4X & | NEWLON-87
Jun 6, 2023, 11:34 AM | ROUTINE | ELEVATOR INSPECTION: ELEVATOR UNIT 28, TO THE LEFT OF ENTRANCE - TOP OF ELEVATOR - MONITOR ROPE ROUGE AND SIZE REPLACE WORN SELECTOR TAPE GUIDES | NEWLON-448
Jun 6, 2023, 9:58 AM | ROUTINE | ELEVATOR INSPECTION: SOUTH END, ELEVATOR UNIT 4 - INSIDE OF ELEVATOR - REPLACE "G" BRAILLE/TACTILE PLATE WITH "STAR" *1 BRAILLE/TACTILE PLATE WITH "1 | NEWLON-84
Oct 24, 2023, 6:25 AM | ROUTINE | E) the down side of the escalator is out of order | NEWLON-484
Aug 30, 2024, 11:20 AM | ROUTINE | E) ELEVATOR - (KONE) BUILD 449 ELEVATOR # 2 RIDING VERY ROUGH | NEWLON-449
Aug 26, 2024, 3:17 PM | ROUTINE | P) ELEVATOR #1 IS NOT WORKING | NEWLON-449
Apr 20, 2022, 8:11 AM | ROUTINE | Request deficiencies be addressed from March 25th Elevator Inspection. (See details for deficiencies) | NEWLON-560
Apr 20, 2022, 7:59 AM | ROUTINE | Replace car platform guard (apron) on cart# 1303 bldg. 534E and 534W not less than 48 in. high. | NEWLON-534
Nov 26, 2024, 1:30 PM | ROUTINE | E) North tower elevator is not functioning. | NEWLON-488
Mar 18, 2025, 9:21 AM | ROUTINE | e) Bravo Side Elevator is in operable, and turned off | NEWLON-492
Jan 6, 2025, 2:11 PM | ROUTINE | E)South Tower Elevator, The elevator is showing S on the floor light indicating that it needs to be serviced. | NEWLON-488
Dec 30, 2024, 7:47 AM | ROUTINE | ONLY ELVATOR DOOR NOT SHUTTING PROPERLY | NEWLON-86
Dec 10, 2024, 11:25 AM | ROUTINE | E) Rm 237 Bravo elavators not working | NEWLON-492
Dec 17, 2024, 2:59 PM | ROUTINE | E) Down escalator stopped. Needs to be reset. | NEWLON-484
Oct 22, 2024, 8:46 AM | ROUTINE | E) elevator technician and and inspector to look at both elevators. Last night sailors were stuck and had to be rescued by fire department | NEWLON-434
May 13, 2025, 11:25 AM | ROUTINE | P) EMPLOYEE DROPPED KEYS IN THE ELEVATOR SHAFT. PLEASE SEND ELEVATOR TECH TO RETRIEVE PERSONAL ITEMS. | NEWLON-518
Jun 17, 2025, 7:21 AM | ROUTINE | E) ELEVATORS- BOTH ELEVATOR 1 AND 2, NEED LIGHTS TO BE REPLACED. LIGHTS ARE OFF, NEED NEW ONES. | NEWLON-534
Oct 30, 2023, 12:50 PM | ROUTINE | E) room 133 has reported seeing bugs/cockroaches. need exterminator to asses this. | NEWLON-430
Aug 15, 2022, 8:57 AM | ROUTINE | E)Location: Alpha Elevator Breaker Issue: Per KONE Contractor, a new shunt trip breaker that feeds the alpha elevator is needed. The current shunt t | NEWLON-492
Aug 7, 2025, 10:21 AM | ROUTINE | E)4th deck elevator vestibule, override switch to the right facing the elevator. | NEWLON-592
Aug 7, 2024, 6:27 AM | ROUTINE | 159 First floor South - KONE - Please secure elevator and prop doors open so PWD can install new carpet in elevator. | NEWLON-159
Apr 28, 2025, 2:08 PM | ROUTINE | E) ELEVATOR #3 IS OUT OF SERVICE | NEWLON-449
Aug 7, 2024, 10:39 AM | ROUTINE | B519 Install a 2nd top of- car stop switch that is within reach from the hoist way landing | NEWLON-519
Feb 28, 2025, 7:31 AM | ROUTINE | B499 Change bucket in pit with oil scavanger pump with oil return line to tank in machine room. | NEWLON-499
Feb 28, 2025, 7:27 AM | ROUTINE | B518 Control spaces and shall be located convenient to the access door. | NEWLON-518
Feb 28, 2025, 7:14 AM | ROUTINE | B474 replace missing braille on floors 1,2,3 | NEWLON-474
Aug 7, 2024, 10:47 AM | ROUTINE | B533 Connection Between Car Frame and Platform | NEWLON-533
Aug 7, 2024, 10:36 AM | ROUTINE | B519 (1.14 Ventilation) Repair/replace inoperative ventilation fan in car. | NEWLON-519
Aug 7, 2024, 10:48 AM | ROUTINE | B533 Replace missing handrail in car. | NEWLON-533
Aug 7, 2024, 10:49 AM | ROUTINE | B533 Secure paneling in car. | NEWLON-533
Aug 7, 2024, 10:49 AM | ROUTINE | B533 Install data tags on counter weight as per ASME A17.1 Rule 201.3c. | NEWLON-533
Aug 7, 2024, 10:50 AM | ROUTINE | B533 Install grate over sump pump hole in pit as per ASME A17.1 Rule 106.1b(4). | NEWLON-533
Aug 7, 2024, 10:51 AM | ROUTINE | B533 Repair toe guard on first floor front door. | NEWLON-533
Aug 7, 2024, 10:52 AM | ROUTINE | B533 Secure car top emergency exit as per ASME A17.1, Rule 204.1e. | NEWLON-533
Aug 7, 2024, 10:53 AM | ROUTINE | B533 Shorten governor rope. | NEWLON-533
Aug 7, 2024, 10:54 AM | ROUTINE | B533 Replace defective car roller guides. | NEWLON-533
Aug 7, 2024, 11:04 AM | ROUTINE | B592 (1.14 Ventilation) Repair/replace inoperative ventilation fan in car. | NEWLON-592
Aug 7, 2024, 10:30 AM | ROUTINE | B519 Adj restrictor. | NEWLON-519
Aug 7, 2024, 10:34 AM | ROUTINE | B519 Install Phase II Fire Fighting Service (FFS) instructional sign. | NEWLON-519
Aug 7, 2024, 10:35 AM | ROUTINE | B519 Install crosshead data plate | NEWLON-519
May 20, 2025, 2:12 PM | ROUTINE | B429E Elevator 18. Replace cab flourescent lamps. Several not working. | NEWLON-429
May 20, 2025, 2:16 PM | ROUTINE | B434E Elevator 22. Escape hatch false ceiling panel needs to be secured with a chain or cable to prevent from falling into car. | NEWLON-434
May 20, 2025, 2:19 PM | ROUTINE | B492-1 Elevator 44. (1.12 Car Enclosure) Repair/replace in car handrail. | NEWLON-492
May 20, 2025, 2:21 PM | ROUTINE | B492-2 Elevator 45. (1.12 Car Enclosure) Repair/replace in car handrail. | NEWLON-492
May 20, 2025, 2:25 PM | ROUTINE | B492-2 Elevator 45. Car Door Interlock. Restrictor needs adj. | NEWLON-492
May 20, 2025, 2:27 PM | ROUTINE | B492-2 Elevator 45. Oil line leaking | NEWLON-492
May 20, 2025, 2:29 PM | ROUTINE | B492-3 Elevator 46. (1.15 Signs and Operating Device Symbols) Install Phase II Fire Fighting Service (FFS) instructional sign. | NEWLON-492
May 20, 2025, 2:31 PM | ROUTINE | B492-3 Elevator 46. (1.3 Operating Control Device) Repair/replace missing panel. | NEWLON-492
May 20, 2025, 2:33 PM | ROUTINE | B492-3 Elevator 46. Restrictor needs adjustment. | NEWLON-492
May 20, 2025, 2:37 PM | ROUTINE | B492-3 Elevator 46. Repair inoperative car lighting. (1.5 car lighting and receptacles) | NEWLON-492
May 20, 2025, 2:39 PM | ROUTINE | B534E Elevator 52. Repair inoperative access circuit top floor. | NEWLON-534
May 20, 2025, 2:40 PM | ROUTINE | B534E Elevator 52. install counter weight sign on counter weight guard | NEWLON-534
May 20, 2025, 2:42 PM | ROUTINE | B534E Elevator 52. Repair inoperative locking bar switch on top of car. | NEWLON-534
May 20, 2025, 2:43 PM | ROUTINE | B534W Elevator 53. "Unintended movement failed. Recommend extending/replacing platform guard to 48"". ASME 17.1 2.19.2.2(4)b" | NEWLON-534
May 20, 2025, 2:45 PM | ROUTINE | B534W Elevator 53. install sign on CWT guard | NEWLON-534
May 20, 2025, 2:46 PM | ROUTINE | B560 Elevator 54. Counterweight runby 5.5". (shorten ropes) | NEWLON-560
May 20, 2025, 2:48 PM | ROUTINE | B560 Elevator 54. Install guards on driving machine sheaves and ropes... See Long Description | NEWLON-560
May 20, 2025, 2:49 PM | ROUTINE | B560 Elevator 54. Furnish laminated wiring diagrams | NEWLON-560
Mar 18, 2025, 9:11 AM | ROUTINE | E) Alpha Side Elevators are in operable, and turned off | NEWLON-492
Apr 28, 2025, 11:19 AM | ROUTINE | freight elevator is Out of Service due to power outage on 4/27/2025 | NEWLON-484
May 14, 2025, 3:13 PM | ROUTINE | E) REQUEST THE FOLLOWING REPAIRS TO THE ELEVATOR: 1. Bevel projections in hoist way as per ASME A17.1 Requirement 2.1.6.2. 2. Install fall protection | NEWLON-87
Jan 28, 2025, 8:15 AM | ROUTINE | E)*KONE* Install missing lighting diffusers in car as per ASME A17.1 Rule 204.7 Elevator | NEWLON-518