## UST-Inventory_M
MARION UNDERGROUND STORAGE TANK PROGRAM STANDARD WORKSHEET
IDEM Facility ID Number: 6971
|  | Last Notification Accepted: | 2024-05-16
Notification UST Number | 1 | 2 | 3 | 4 | 5 | 6
Owner UST Number | B76-1 (East Tank) | B76-1 (West Tank) | B5 | B175 | B55 | 18
Basic Information
Location | Outside Bldg. 76 (south side) | Outside Bldg. 76 (south side) | Outside Bldg. 5 (south side) | Outside Bldg. 138/175 (north side) | Outside Bldg. 55 (south side) | Formerly Outside Bldg. 18
Product Type | No. 2 Fuel Oil | No. 2 Fuel Oil | Diesel | Diesel | Gasoline | Diesel
Purpose | Fuel for On-site Boilers | Fuel for Emergency Generator | Fuel for Emergency Generator | Fuel for Emergency Generator | Vehicle/Equipment Fueling | Fuel for Emergency Generator
Status | Active | Active | Temporarily Closed - Emptied | Active | Temporarily Closed - Emptied | Closed
Installation Date | 2013-10-16 | 2013-10-16 | 1992-07-15 | 1993-09-28 | 1992-06-08 | 1992-08-06
Responsible Person
Responsible VANIHCS Personnel | Boiler Plant Manager | Boiler Plant Manager | Maintanence & Operations Section | Maintanence & Operations Section | Maintanence & Operations Section
Regulatory Applicability
Indiana UST Program | Not Regulated - Exempt from definition of "underground storage tank" and therefore the requirements under Indiana's UST program [see 329 IAC 9-1-1(c), which incorporates by reference the definitions from 40 CFR 280.12]. | Not Regulated - Exempt from definition of "underground storage tank" and therefore the requirements under Indiana's UST program [see 329 IAC 9-1-1(c), which incorporates by reference the definitions from 40 CFR 280.12]. | Not Regulated - Tank emptied. No longer subject to the technical requirements outlined in Subpart C and D. (40 CFR 280.70(a)). Vent lines must remain open and functional. All other lines, pumps, manways, and ancillary equipment must be capped and secured. | Fully Regulated - Subject to all technical requirements outlined in Subpart D of 40 CFR 280. [incorporating by reference 40 CFR 280.10(a)(1)(ii)]. | Not Regulated - Tank emptied. No longer subject to the technical requirements outlined in Subpart C and D. (40 CFR 280.70(a)). Vent lines must remain open and functional. All other lines, pumps, manways, and ancillary equipment must be capped and secured. | Not Regulated - Permanently removed from ground on September 16, 2013.
SPCC Plan | Regulated - Subject to SPCC requirements since USTs "used for storing heating oil for consumptive use on the premises where stored" are exempt from the definition of "underground storage tank" under 329 IAC 9-1-1(c) [incorporating by reference 40 CFR 280.12]. | Regulated - Subject to SPCC requirements since USTs "used for storing heating oil for consumptive use on the premises where stored" are exempt from the definition of "underground storage tank" under 329 IAC 9-1-1(c) [incorporating by reference 40 CFR 280.12]. | Not Regulated - Exempt from SPCC requirements under 40 CFR 112.1(b)(3) due to being defined as "permanently closed". | Not Regulated - Exempt from SPCC requirements under 40 CFR 112.1(d)(2)(i) due to being subject to all the technical requirements under Indiana's UST program. | Not Regulated - Exempt from SPCC requirements under 40 CFR 112.1(b)(3) due to being defined as "permanently closed". | Not Regulated - Permanently removed from ground on September 16, 2013.
Tank Information
Type | Double-walled | Double-walled | Double-walled | Double-walled | Double-walled | Double-walled
Material | Fiberglass | Fiberglass | Fiberglass | Fiberglass | Fiberglass | Fiberglass
Capatible w/ Product Type Stored | Yes | Yes | Yes | Yes | Yes
Nominal Capacity (gallons) | 30000 | 30000 | 1000 | 15000 | 10000 | 10000
Compartmented / Manifolded? | No | No | No | No | No
Corrosion Protection | Non-corrodible Material | Non-corrodible Material | Non-corrodible Material | Non-corrodible Material | Non-corrodible Material
Piping Information
Type | European Suction | European Suction | American Suction | European Suction | European Suction | American Suction
| Double-walled | Double-walled | Double-walled | Double-walled | Double-walled | Double-walled
Material | Fiberglass | Fiberglass | Flexible Composite | Flexible Composite | Flexible Composite | Fiberglass
Manufacturer |  |  | Franklin Electric | Franklin Electric
Model |  |  | APT XP | APT XP
Date Piping Installed / Repaired |  |  | 2019-09-18 | 2019-09-18
Corrosion Protection | Non-corrodible Material | Non-corrodible Material | Non-corrodible Material | Non-corrodible Material | Non-corrodible Material
Piping Repairs | Must be repaired in accordance with manufacturer's specifications [40 CFR 280.33(c)] | Must be repaired in accordance with manufacturer's specifications [40 CFR 280.33(c)] | Must be repaired in accordance with manufacturer's specifications [40 CFR 280.33(c)] | Must be repaired in accordance with manufacturer's specifications [40 CFR 280.33(c)] | Must be repaired in accordance with manufacturer's specifications [40 CFR 280.33(c)]
Notes | After April 11, 2016, if a facility repairs 50% or more piping in a single piping run, entire piping run must be removed and secondarily contained piping must be installed.
Release Detection Information
Equipment | INCON Franklin Fueling Systems TS-550 with Probes | INCON Franklin Fueling Systems TS-550 with Probes | Veeder Root TLS4 (Tank Emptied) | Veeder Root TLS4 | Veeder Root TLS4 (Tank Emptied)
Primary UST Release Detection [40 CFR 280.43] |  |  |  | ATG Continuous Statistical Leak Detection (CSLD)
Secondary UST Release Detection [40 CFR 280.43] |  |  |  | ATG Interstitiual Monitoring
Primary Piping Release Detection [40 CFR 280.44] |  |  |  | ATG Continuous In-Tank Leak Detection (CITLDS)
Secondary Piping Release Detection [40 CFR 280.44] |  |  |  | 3-year Line Tightness Testing
Notes |  |  | Not required - tank emptied and temporarily closed. |  | Not required - tank emptied and temporarily closed.
Release Detection Inspection/Testing Requirements
Annual Operation Testing |  |  |  | At least annually, check release detection equipment for proper operation. [40 CFR 280.40(a)(3)] Automatic tank gauge and other controllers: test the alarms, verify system configuration, and test battery backup. Probes and sensors: inspect for residual buildup, ensure floats move freely, ensure shaft is not damaged, ensure cables are free of kinks and breaks, and test alarm operability and communication with controller. Automatic line leak detector: ensure the device activates (alarms, restricts flow, or shuts off flow) within an hour when simulating a release equivalent to 3 gallons per hour to 10 pounds per square inch Vacuum pumps and pressure gauges: Ensure proper communication with sensors and controller Hand-held electronic sampling equipment associated with groundwater and vapor monitoring: ensure device operates properly.
Annual Test Requirements for Release Detection Components |  |  |  | The following code of practice must be used to comply with paragraph (a)(3) of this section: Petroleum Equipment Institute Publication RP1200, “Recommended Practices for the Testing and Verification of Spill, Overfill, Leak Detection and Secondary Containment Equipment at UST Facilities”.
Walkthrough Inspection |  |  |  | Every 30 days check to make sure the release detection equipment is operating with no alarms or other unusual operating conditions present; and ensure records of release detection testing are reviewed and current [40 CFR 280.36(a)(1)(i)(B)] Annually check any hand held release detection equipment such as tank gauge sticks for operability and serviceability; [40 CFR 280.36(a)(1)(ii)(B)] Annually check sumps (used for release detection) for damage, leaks to the containment area, or releases to the environment; and remove liquid or debris. Double walled containment sumps with interstitial monitoring to check for a leak in the intersitial area. [40 CFR 280.36(a)(1)(ii)(A)]
Line tightness testing for Suction Piping |  |  |  | A line tightness test must be conducted at least every 3 years and a periodic test of piping may be conducted only if it can detect a 0.1 gallon per hour leak rate at one and one-half times the operating pressure. [40 CFR 280.41(b)(1)(ii)]
Tightness Testing for Sumps Used in Release Detection Monitoring |  |  |  | Test every 3 years to ensure equipment is liquid tight by using vacuum, pressure, or liquid testing. [40 CFR 280.35(a)(1)(ii)]
Tightness Testing of Repairs |  |  |  | All repairs to underground storage tanks and piping must be tightness tested in accordance with 40 CFR §280.43(c) and 280.44(b) within 30 days following the date of the completion of the repair UNLESS: 1. The repaired tank is internally inspected in accordance with a code of practice developed by a nationally recognized association or an independent testing laboratory 2. The repaired portion of the UST system is monitored monthly for releases in accordance with a method specified in 40 CFR 280.43(d) through (i)
Recordkeeping |  |  |  | Release detection monitoring results - keep for 1 year [40 CFR 280.45(b)]
Annual operation test records - keep for 3 year. Records must include a list of each area checked, whether each area checked was acceptable or needed action taken, and a description of actions taken to correct an issue. [40 CFR 280.45(b)(1)]
Walkthrough inspections records - keep for 1 year. Records must include a list of each area checked, whether each area checked was acceptable or needed action taken, and a description of actions taken to correct an issue. [40 CFR 280.36(b)]
Tank Tightness Test Results - Until the next test. [40 CFR 280.45(b)(2)]
Containment sump tightness testing records - keep for 3 years. [40 CFR 280.45(b)(1)]
Manufacturer's Information (i.e. performance claim & maintenance schedules) - keep for 5 years after installation.
Calibration/maintenance/repair records - keep for 1 year after the servicing work is completed.
Spill Protection Information
Equipment | Spill Catchment Basin (single walled) | Spill Catchment Basin (single walled) | Spill Catchment Basin (single walled) | Spill Catchment Basin (double walled) | Spill Catchment Basin (single walled)
Date Installed |  |  | 2009-02-01 | 2010-05-01
Manufacturer |  |  | Franklin Electric | EMCO | OPW
Model |  |  | EBW 705-54X | A1004EVR-317SS | 1C-2105
Periodic Testing |  |  | Not required - tank emptied and temporarily closed. | Test every 3 years to ensure equipment is liquid tight by using vacuum, pressure, or liquid testing. [40 CFR 280.35(a)(1)] | Not required - tank emptied and temporarily closed.
Walkthrough Inspection |  |  |  | Every 30 days visually check for: Damage and remove liquid or debris; check for and remove obstructions in the fill pipe; and check the fill cap to make sure it is securely on the fill pipe. For double-walled spill prevention equipment with interstitial monitoring, check for a leak in the interstitial area. [40 CFR 280.36(a)(1)(i)(A)]
Recordkeeping |  |  |  | Spill Protection testing records - keep for 3 years. [40 CFR 280.35(c)(1)]
Documentation showing spill prevention equipment and containment sumps used for interstitial monitoring of piping is double-walled and the integrity of both walls is periodically monitored: Keep for as long as periodic measuring is conducted. [40 CFR 280.35(c)(2)]***
Records of maintenance, repair, and calibration of on-site release detection equipment: One year after servicing is complete. [40 CFR 280.45(c)]
Walkthrough inspection records - keep for 1 year. Records must include a list of each area checked, whether each area checked was acceptable or needed action taken, a description of actions taken to correct an issue, and delivery records if spill prevention equipment is checked less frequently than every 30 days due to infrequent deliveries. [40 CFR 280.36(b)]
Overfill Prevention Information
Primary Overfill Prevention Equipment |  |  | Auto Shutoff / Flapper | Auto Shutoff / Flapper | Auto Shutoff / Flapper
Date Installed
Manufacturer |  |  | OPW | OPW
Model |  |  | 71SO | 71SO
Secondary Overfill Prevention Equipment |  |  | N/A | N/A | N/A
Under Dispenser Containment Present? |  |  | No | No | Yes - Not Testable
Periodic Testing |  |  |  | Test every 3 years to ensure equipment is set to activates at the correct level and will activate when the regulated substance reaches that level. [40 CFR 280.35(a)(2)]
Recordkeeping |  |  |  | Overfill Prevention Equipment test records - keep for 3 years. [40 CFR 280.35(c)(1)]
Operation and Maintenance
Walkthrough Inspection |  |  |  | Conducted in conjuntion with monthly release, spill equipment, and overfill walkthrough inspections. Facility to utilize Petroleum Equipment Institute Recommended Practice RP 900, "Recommended Practices for the Inspection and Maintenance of UST Systems" form to comply with 40 CFR 280.36(a)(2).
Operator Training Requirements
Designated Operators |  |  | All owners and operators of UST systems must ensure they have designated Class A, Class B, and Class C operators. -At least one Class A and one Class B operator for each UST or group of USTs at a facility; [40 CFR 280.241(a)] Class A and Class B operators designated after October 13, 2018 must meet requirements in § 280.242 within 30 days of assuming duties. -Each individual who meets the definition of Class C operator at the UST facility as a Class C operator. Class C operators designated after October 13, 2018 must be trained before assuming duties of a Class C operator
Retraining Requirements |  |  | Operators may need to be retrained if the UST system is not in compliance. [40 CFR 280.244]
Recordkeeping |  |  | For as long as the operated is designated at the facility. [40 CFR 280.34(b)(9)]
Other Recordkeeping
Repair Records |  |  | Maintain until the UST is permanently closed or undergoes a change-in-service. [40 CFR 280.71)
Tank Closure Records |  |  | Records of the site assessment results required for permanent closure: 3 Years after closing an UST. [40 CFR 280.74]
Training Records |  |  | A list of currently designated operators trained for each facility and proof of training or retraining for each operator. [40 CFR 280.245]
Notification Records |  |  | (1) Notification for all UST systems (§ 280.22), which includes certification of installation for new UST systems (§ 280.20(e)) and notification when any person assumes ownership of an UST system (§ 280.22(b)); (2) Notification prior to UST systems switching to certain regulated substances (§ 280.32(b)); (3) Reports of all releases including suspected releases (§ 280.50), spills and overfills (§ 280.53), and confirmed releases (§ 280.61); (4) Corrective actions planned or taken including initial abatement measures (§ 280.62), initial site characterization (§ 280.63), free product removal (§ 280.64), investigation of soil and groundwater cleanup (§ 280.65), and corrective action plan (§ 280.66); and (5) A notification before permanent closure or change-in-service (§ 280.71).
Compatibility Documentation |  |  | Owners and operators must use an UST system made of or lined with materials that are compatible with the substance stored in the UST system. Demonstrate compatibility of the UST system (including the tank, piping, containment sumps, pumping equipment, release detection equipment, spill equipment, and overfill equipment). Owners and operators may demonstrate compatibility of the UST system by using one of the following options: (i) Certification or listing of UST system equipment or components by a nationally recognized, independent testing laboratory for use with the regulated substance stored; or (ii) Equipment or component manufacturer approval. The manufacturer's approval must be in writing, indicate an affirmative statement of compatibility, specify the range of biofuel blends the equipment or component is compatible with, and be from the equipment or component manufacturer. [40 CFR 280.32]
Gray areas = Not Applicable Red areas = Missing Information

## UST-Inventory_FW
FORT WAYNE UNDERGROUND STORAGE TANK PROGRAM STANDARD WORKSHEET
IDEM Facility ID Number: 18029
| Last Notification Accepted: | 2024-03-13
Notification UST Number | 1 | 2 | 3 | 4
Owner UST Number | Diesel East | Diesel West | Gasoline | B16 Gen
Basic Information
Location | Outside Bldg. 2 (Boiler Plant) | Outside Bldg. 2 (Boiler Plant) | Outside Bldg. 2 (Boiler Plant) | Outside Bldg. 16
Product Type | Diesel | Diesel | Gasoline | Diesel
Purpose | Fuel for On-site Boilers and Emergency Generator | Fuel for On-site Boilers and Emergency Generator | Vehicle/Equipment Fueling | Fuel for Emergency Generator
Status | Active | Active | Active | Active
Installation Date | 1998-12-01 | 1998-12-01 | 1994-08-01 | 1982-01-01
Responsible Person
Responsible VANIHCS Personnel | Maintanence & Operations Section | Maintanence & Operations Section | Maintanence & Operations Section | Maintanence & Operations Section
Regulatory Applicability
Indiana UST Program | Fully Regulated - Subject to all technical requirements under Indiana's UST program (329 IAC Art. 9). | Fully Regulated - Subject to all technical requirements under Indiana's UST program (329 IAC Art. 9). | Fully Regulated - Subject to all technical requirements under Indiana's UST program (329 IAC Art. 9). | Fully Regulated - Subject to all technical requirements outlined in Subpart D of 40 CFR 280. [incorporating by reference 40 CFR 280.10(a)(1)(ii)].
SPCC Plan | Not Regulated - Exempt from SPCC requirements under 40 CFR 112.1(d)(2)(i) due to being subject to all the technical requirements under Indiana's UST program. | Not Regulated - Exempt from SPCC requirements under 40 CFR 112.1(d)(2)(i) due to being subject to all the technical requirements under Indiana's UST program. | Not Regulated - Exempt from SPCC requirements under 40 CFR 112.1(d)(2)(i) due to being subject to all the technical requirements under Indiana's UST program. | Not Regulated - Exempt from SPCC requirements under 40 CFR 112.1(d)(2)(i) due to being subject to all the technical requirements under Indiana's UST program.
Tank Information
Type | Double-walled | Double-walled | Double-walled | Double-walled
Material | Fiberglass | Fiberglass | Fiberglass | Fiberglass
Capatible w/Product Type Stored | Yes | Yes | Yes | Yes
Nominal Capacity (gallons) | 12000 | 12000 | 1000 | 2000
Compartmented / Manifolded? | No | No | No | No
Corrosion Protection | Non-corrodible Material | Non-corrodible Material | Non-corrodible Material | Non-corrodible Material
Piping Information
Type | European Suction | Pressurized | Pressurized | European Suction
| Double-walled | Double-walled | Double-walled | Double-walled
Material | Flexible Composite | Flexible Composite | Flexible Composite | Flexible Composite
Manufacturer | OPW | OPW | OPW | OPW
Model | FlexWorks | FlexWorks | FlexWorks | FlexWorks
Date Piping Installed / Repaired | 2023-10-01 | 2023-10-01 | 2023-10-01 | 2009-08-01
Corrosion Protection | Non-corrodible Material | Non-corrodible Material | Non-corrodible Material | Non-corrodible Material
Under Dispenser Containment Present? | No | No | Yes - Testable | No
Manufacturer |  |  | OPW
Date Installed |  |  | 2023-10-01
Submersible Turbine Pump Present? | No | Yes - Testable | Yes - Testable | No
Manufacturer |  | FE Petro 3/4 HP | FE Petro 3/4 HP
Date Installed |  | 10/01/2023 | 10/01/2023
Piping Repairs | Must be repaired in accordance with manufacturer's specifications [40 CFR 280.33(c)] | Must be repaired in accordance with manufacturer's specifications [40 CFR 280.33(c)] | Must be repaired in accordance with manufacturer's specifications [40 CFR 280.33(c)] | Must be repaired in accordance with manufacturer's specifications [40 CFR 280.33(c)]
Notes | After April 11, 2016, if a facility repairs 50% or more piping in a single piping run, entire piping run must be removed and secondarily contained piping must be installed.
Release Detection Information
Equipment | INCON Franklin Fueling Systems TS-550 evo with Probes (installed 11/2013) | INCON Franklin Fueling Systems TS-550 evo with Probes (installed 11/2013) | INCON Franklin Fueling Systems TS-550 evo with Probes (installed 11/2013) | INCON Franklin Fueling Systems TS-550 evo with Probes (installed 11/2013)
Primary UST Release Detection [40 CFR 280.43] | ATG Continuous Statistical Leak Detection (CSLD) | ATG Continuous Statistical Leak Detection (CSLD) | ATG Continuous Statistical Leak Detection (CSLD) | ATG Continuous Statistical Leak Detection (CSLD)
Secondary UST Release Detection [40 CFR 280.43] | ATG Interstitial Monitoring | ATG Interstitial Monitoring | ATG Interstitial Monitoring | ATG Interstitial Monitoring
Model (Probes) | FMP-EIS | FMP-EIS | FMP-EIS | FMP-EIS
Primary Piping Release Detection [40 CFR 280.44] | Not required. [40 CFR 280.41(b)(1)(ii)] | Annual Line Tightness Testing | Annual Line Tightness Testing | Not required. [40 CFR 280.41(b)(1)(ii)]
Secondary Piping Release Detection [40 CFR 280.44] | None Required (Safe Suction) | ELLD w/Annual Testing | ELLD w/Annual Testing | None Required (Safe Suction)
Manufacturer |  | Vaporless | FE Petro
Model |  | 99 LD-2000 | STP-MLD-SGL
Notes |  | Automatic Line Leak Detectors: Methods which alert the operator to the presence of a leak by restricting or shutting off the flow of regulated substances through piping or triggering an audible or visual alarm may be used only if they detect leaks of 3 gallons per hour at 10 pounds per square inch line pressure within 1 hour. [40 CFR 280.44(a)] | Automatic Line Leak Detectors: Methods which alert the operator to the presence of a leak by restricting or shutting off the flow of regulated substances through piping or triggering an audible or visual alarm may be used only if they detect leaks of 3 gallons per hour at 10 pounds per square inch line pressure within 1 hour. [40 CFR 280.44(a)]
Repairs | Repairs to secondary containment areas of tanks, piping, and containment sumps used for interstitual monitoring must have the secondary containment tested for tightness within 30 days following the date of repair. Except if the repair is internally inspected in accordance with a code of practice or the repaired portion is monitored monthly for releases. [40 CFR 280.33(d)]
Release Detection Inspections/Testing Requirements
Annual Operation Testing | At least annually, check release detection equipment for proper operation. [40 CFR 280.40(a)(3)] Automatic tank gauge and other controllers: test the alarms, verify system configuration, and test battery backup. Probes and sensors: inspect for residual buildup, ensure floats move freely, ensure shaft is not damaged, ensure cables are free of kinks and breaks, and test alarm operability and communication with controller. Automatic line leak detector: ensure the device activates (alarms, restricts flow, or shuts off flow) within an hour when simulating a release equivalent to 3 gallons per hour to 10 pounds per square inch. Only applicable for the Diesel West and Gasoline tank.
Annual Test Requirements for Release Detection Components | The following code of practice must be used to comply with paragraph (a)(3) of this section: Petroleum Equipment Institute Publication RP1200, “Recommended Practices for the Testing and Verification of Spill, Overfill, Leak Detection and Secondary Containment Equipment at UST Facilities”.
Walkthrough Inspection | Every 30 days check to make sure the release detection equipment is operating with no alarms or other unusual operating conditions present; and ensure records of release detection testing are reviewed and current [40 CFR 280.36(a)(1)(i)(B)] Annually check any hand held release detection equipment such as tank gauge sticks for operability and serviceability; [40 CFR 280.36(a)(1)(ii)(B)] Annually check sumps (used for release detection) for damage, leaks to the containment area, or releases to the environment; and remove liquid or debris. Double walled containment sumps with interstitial monitoring to check for a leak in the intersitial area. [40 CFR 280.36(a)(1)(ii)(A)]
Line tightness testing for Piping | Not required for Safe Suction piping. | Pressurized Piping line tightness testing is satisfied through interstitual monitoring, if designed to detect a release from any portion of the underground piping, if not, an annual tightness test will need conducted. [40 CFR 280.41(b)(1)(i)(B)] | Pressurized Piping line tightness testing is satisfied through interstitual monitoring, if designed to detect a release from any portion of the underground piping, if not, an annual tightness test will need conducted. [40 CFR 280.41(b)(1)(i)(B)] | Not required for Safe Suction piping.
Tightness Testing of Repairs | All repairs to underground storage tanks and piping must be tightness tested in accordance with 40 CFR §280.43(c) and 280.44(b) within 30 days following the date of the completion of the repair UNLESS: 1. The repaired tank is internally inspected in accordance with a code of practice developed by a nationally recognized association or an independent testing laboratory 2. The repaired portion of the UST system is monitored monthly for releases in accordance with a method specified in 40 CFR 280.43(d) through (i)
Recordkeeping | Release detection monitoring results - keep for 1 year [40 CFR 280.45(b)]
Annual operation test records - keep for 3 year. Records must include a list of each area checked, whether each area checked was acceptable or needed action taken, and a description of actions taken to correct an issue. [40 CFR 280.45(b)(1)]
Walkthrough inspections records - keep for 1 year. Records must include a list of each area checked, whether each area checked was acceptable or needed action taken, and a description of actions taken to correct an issue. [40 CFR 280.36(b)]
Tank Tightness Test Results - Until the next test. [40 CFR 280.45(b)(2)]
Containment sump tightness testing records - keep for 3 years. [40 CFR 280.45(b)(1)]
Manufacturer's Information (i.e. performance claim & maintenance schedules) - keep for 5 years after installation.
Calibration/maintenance/repair records - keep for 1 year after the servicing work is completed.
Spill Protection Information
Equipment | Secondary Contained Spill Bucket (double walled) | Secondary Contained Spill Bucket (double walled) | Secondary Contained Spill Bucket (double walled) | Secondary Contained Spill Bucket (double walled)
Date Installed | 2023-10-01 | 2023-10-01 | 2023-10-01 | 2009-08-01
Manufacturer | OPW | OPW | OPW | OPW
Model | 1-2105 | 1-2105 | 1-2105
Periodic Testing | Test every 3 years to ensure equipment is liquid tight by using vacuum, pressure, or liquid testing. [40 CFR 280.35(a)(1)]
Walkthrough Inspection | Every 30 days visually check for: Damage and remove liquid or debris; check for and remove obstructions in the fill pipe; and check the fill cap to make sure it is securely on the fill pipe. For double-walled spill prevention equipment with interstitial monitoring, check for a leak in the interstitial area. [40 CFR 280.36(a)(1)(i)(A)]
Spill Equipment Repairs | Within 30 days following any repair to spill equipment, the repaired spill equipment must be tested or inspected to ensure equipment is operating properly and will prevent released to the environment. [40 CFR 280.33(f)]
Recordkeeping | Spill Protection testing records - keep for 3 years. [40 CFR 280.35(c)(1)]
Documentation showing spill prevention equipment and containment sumps used for interstitial monitoring of piping is double-walled and the integrity of both walls is periodically monitored: Keep for as long as periodic measuring is conducted. [40 CFR 280.35(c)(2)]***
Records of maintenance, repair, and calibration of on-site release detection equipment: One year after servicing is complete. [40 CFR 280.45(c)]
Walkthrough inspection records - keep for 1 year. Records must include a list of each area checked, whether each area checked was acceptable or needed action taken, a description of actions taken to correct an issue, and delivery records if spill prevention equipment is checked less frequently than every 30 days due to infrequent deliveries. [40 CFR 280.36(b)]
Overfill Prevention Information
Primary Overfill Prevention Equipment | Auto Shutoff / Flapper | Auto Shutoff / Flapper | Auto Shutoff / Flapper | Auto Shutoff / Flapper
Date Installed | 10/01/2023 | 10/01/2023 | 10/01/2023 | 08/01/2009
Manufacturer | OPW | OPW | OPW
Model | 61SO | 61SOC | 61SO
Secondary Overfill Prevention Equipment | Overfill Alarm (ATG) | Overfill Alarm (ATG) | Overfill Alarm (ATG) | Overfill Alarm (ATG)
Periodic Testing | Test every 3 years to ensure equipment is set to activates at the correct level and will activate when the regulated substance reaches that level. [40 CFR 280.35(a)(2)]
Overfill Prevention Equipment Repairs | Within 30 days following any repair to spill equipment, the repaired spill equipment must be tested or inspected to ensure equipment is set to activate at the correct level and will activate when the regulated substance reaches that level [40 CFR 280.33(f)]
Recordkeeping | Overfill Prevention Equipment test records - keep for 3 years. [40 CFR 280.35(c)(1)]
Operation and Maintenance
Walkthrough Inspection | Conducted in conjuntion with monthly release, spill equipment, and overfill walkthrough inspections. Facility to utilize Petroleum Equipment Institute Recommended Practice RP 900, "Recommended Practices for the Inspection and Maintenance of UST Systems" form to comply with 40 CFR 280.36(a)(2).
Operator Training Requirements
Designated Operators | All owners and operators of UST systems must ensure they have designated Class A, Class B, and Class C operators. -At least one Class A and one Class B operator for each UST or group of USTs at a facility; [40 CFR 280.241(a)] Class A and Class B operators designated after October 13, 2018 must meet requirements in § 280.242 within 30 days of assuming duties. -Each individual who meets the definition of Class C operator at the UST facility as a Class C operator. Class C operators designated after October 13, 2018 must be trained before assuming duties of a Class C operator
Retraining Requirements | Operators may need to be retrained if the UST system is not in compliance. [40 CFR 280.244]
Recordkeeping | For as long as the operated is designated at the facility. [40 CFR 280.34(b)(9)]
Other Recordkeeping
Repair Records | Maintain until the UST is permanently closed or undergoes a change-in-service. [40 CFR 280.71)
Tank Closure Records | Records of the site assessment results required for permanent closure: 3 Years after closing an UST. [40 CFR 280.74]
Training Records | A list of currently designated operators trained for each facility and proof of training or retraining for each operator. [40 CFR 280.245]
Notification Records | (1) Notification for all UST systems (§ 280.22), which includes certification of installation for new UST systems (§ 280.20(e)) and notification when any person assumes ownership of an UST system (§ 280.22(b)); (2) Notification prior to UST systems switching to certain regulated substances (§ 280.32(b)); (3) Reports of all releases including suspected releases (§ 280.50), spills and overfills (§ 280.53), and confirmed releases (§ 280.61); (4) Corrective actions planned or taken including initial abatement measures (§ 280.62), initial site characterization (§ 280.63), free product removal (§ 280.64), investigation of soil and groundwater cleanup (§ 280.65), and corrective action plan (§ 280.66); and (5) A notification before permanent closure or change-in-service (§ 280.71).
Compatibility Documentation | Owners and operators must use an UST system made of or lined with materials that are compatible with the substance stored in the UST system. Demonstrate compatibility of the UST system (including the tank, piping, containment sumps, pumping equipment, release detection equipment, spill equipment, and overfill equipment). Owners and operators may demonstrate compatibility of the UST system by using one of the following options: (i) Certification or listing of UST system equipment or components by a nationally recognized, independent testing laboratory for use with the regulated substance stored; or (ii) Equipment or component manufacturer approval. The manufacturer's approval must be in writing, indicate an affirmative statement of compatibility, specify the range of biofuel blends the equipment or component is compatible with, and be from the equipment or component manufacturer. [40 CFR 280.32]
Gray areas = Not Applicable Red areas = Missing Information